## Case_Create
Case | Run_test | Test_Type | Target POC V | ActiveP | ReactiveP | SCR | X_R | Vsource_i | PPC_Vref | Trf_Tap | SF_P | SF_Q | BESS_P | BESS_Q | POC_Pflat | POC_Qflat | POC_P | POC_Q | Test_File_Names | Shunt(1.15pu) | Shunt(1.2pu) | StateCASE | Reference Equations | backup shunts
1 | Yes | Case_setup | 1.03 | -1 | 0 | 10 | 3 | 1.0647 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -25.7273 | -1.8201 |  |  | -25.9984 | 0.0102 | PSSE_DMAT_BESSC_SCR10_XR3_P-1_Q0 | 34.7613 | 47.3930 | DMAT Charging | BESS Charging
2 | Yes | Case_setup | 1.03 | -1 | 0 | 10 | 14 | 1.0414 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -25.7271 | -1.8131 |  |  | -25.9981 | 0.0178 | PSSE_DMAT_BESSC_SCR10_XR14_P-1_Q0 | 33.5196 | 44.8509 | DMAT Charging
3 | Yes | Case_setup | 1.03 | -1 | 0.3 | 10 | 14 | 1.0126 | 1.0452 | 1.0375 | 0.0000 | 0.0000 | -25.7057 | 6.5246 |  |  | -25.9984 | 7.8166 | PSSE_DMAT_BESSC_SCR10_XR14_P-1_Q0.3 | 33.1102 | 44.3128 | DMAT Charging
4 | Yes | Case_setup | 1.03 | -1 | -0.3 | 10 | 14 | 1.0701 | 1.0148 | 0.9750 | 0.0000 | -0.0000 | -25.7025 | -9.2532 |  |  | -26.0024 | -7.7850 | PSSE_DMAT_BESSC_SCR10_XR14_P-1_Q-0.3 | 33.8025 | 45.8670 | DMAT Charging
5 | Yes | Case_setup | 1.03 | -1 | 0 | 3 | 14 | 1.1013 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -25.7294 | -1.8184 |  |  | -26.0005 | 0.0114 | PSSE_DMAT_BESSC_SCR3_XR14_P-1_Q0 | 14.5560 | 19.8472 | DMAT Charging
6 | Yes | Case_setup | 1.03 | -1 | 0 | 3 | 3 | 1.1731 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -25.7269 | -1.8228 |  |  | -25.9980 | 0.0077 | PSSE_DMAT_BESSC_SCR3_XR3_P-1_Q0 | 14.8183 | 21.4441 | DMAT Charging
7 | Yes | Case_setup | 1.03 | -1 | 0.3 | 3 | 3 | 1.0936 | 1.0452 | 1.0375 | 0.0000 | -0.0000 | -25.7028 | 6.5141 |  |  | -25.9953 | 7.8071 | PSSE_DMAT_BESSC_SCR3_XR3_P-1_Q0.3 | 14.4448 | 19.7216 | DMAT Charging
8 | Yes | Case_setup | 1.03 | -1 | -0.3 | 3 | 3 | 1.2552 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | -25.7037 | -9.2584 |  |  | -26.0037 | -7.7912 | PSSE_DMAT_BESSC_SCR3_XR3_P-1_Q-0.3 | 15.4781 | 18.0623 | DMAT Charging
9 | Yes | Case_setup | 1.03 | -0.05 | 0 | 10 | 14 | 1.0303 | 1.0300 | 1.0000 | -0.0000 | -0.0000 | -1.2780 | -5.6400 |  |  | -1.3031 | 0.0146 | PSSE_DMAT_BESSC_SCR10_XR14_P-0.05_Q0 | 33.6220 | 44.9213 | DMAT Charging
10 | Yes | Case_setup | 1.03 | -0.05 | 0.3 | 10 | 14 | 1.0013 | 1.0452 | 1.0250 | 0.0000 | 0.0000 | -1.2692 | 2.2747 |  |  | -1.2999 | 7.8096 | PSSE_DMAT_BESSC_SCR10_XR14_P-0.05_Q0.3 | 33.3677 | 44.5749 | DMAT Charging
11 | Yes | Case_setup | 1.03 | -0.05 | -0.3 | 10 | 14 | 1.0593 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | -1.2374 | -12.8971 |  |  | -1.3014 | -7.7851 | PSSE_DMAT_BESSC_SCR10_XR14_P-0.05_Q-0.3 | 33.8980 | 41.9002 | DMAT Charging
12 | Yes | Case_setup | 1.03 | -0.05 | 0 | 3 | 14 | 1.0311 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -1.2786 | -5.6364 |  |  | -1.3037 | 0.0184 | PSSE_DMAT_BESSC_SCR3_XR14_P-0.05_Q0 | 14.6675 | 20.0077 | DMAT Charging
13 | Yes | Case_setup | 1.03 | -0.05 | 0 | 3 | 3 | 1.0351 | 1.0300 | 1.0000 | -0.0000 | -0.0000 | -1.2785 | -5.6434 |  |  | -1.3036 | 0.0110 | PSSE_DMAT_BESSC_SCR3_XR3_P-0.05_Q0 | 14.7973 | 21.4977 | DMAT Charging
14 | Yes | Case_setup | 1.03 | -0.05 | 0.3 | 3 | 3 | 0.9443 | 1.0452 | 1.0250 | 0.0000 | 0.0000 | -1.2708 | 2.2543 |  |  | -1.3014 | 7.7897 | PSSE_DMAT_BESSC_SCR3_XR3_P-0.05_Q0.3 | 14.5741 | 19.8902 | DMAT Charging
15 | Yes | Case_setup | 1.03 | -0.05 | -0.3 | 3 | 3 | 1.1272 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | -1.2375 | -12.9004 |  |  | -1.3015 | -7.7889 | PSSE_DMAT_BESSC_SCR3_XR3_P-0.05_Q-0.3 | 14.6222 | 15.8874 | DMAT Charging
16 | Yes | Case_setup | 1.03 | -1 | 0 | 4.53 | 1.21 | 1.1782 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -25.7295 | -1.8403 |  |  | -26.0006 | -0.0107 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-1_Q0 | 20.8690 | 33.6703 | DMAT Charging
17 | Yes | Case_setup | 1.03 | -1 | 0.3 | 4.53 | 1.21 | 1.1358 | 1.0452 | 1.0375 | -0.0000 | -0.0000 | -25.7035 | 6.5141 |  |  | -25.9960 | 7.8067 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-1_Q0.3 | 20.6636 | 37.3683 | DMAT Charging
18 | Yes | Case_setup | 1.03 | -1 | -0.3 | 4.53 | 1.21 | 1.2225 | 1.0148 | 0.9750 | 0.0000 | -0.0000 | -25.7015 | -9.2795 |  |  | -26.0016 | -7.8138 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-1_Q-0.3 | 20.9829 | 28.5138 | DMAT Charging
19 | Yes | Case_setup | 1.03 | -1 | 0 | 7.06 | 1.63 | 1.1081 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -25.7298 | -1.8304 |  |  | -26.0010 | -0.0014 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-1_Q0 | 27.7148 | 37.9231 | DMAT Charging
20 | Yes | Case_setup | 1.03 | -1 | 0.3 | 7.06 | 1.63 | 1.0757 | 1.0452 | 1.0375 | -0.0000 | 0.0000 | -25.7026 | 6.5093 |  |  | -25.9952 | 7.8024 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-1_Q0.3 | 27.4484 | 37.5687 | DMAT Charging
21 | Yes | Case_setup | 1.03 | -1 | -0.3 | 7.06 | 1.63 | 1.1411 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | -25.7045 | -9.2615 |  |  | -26.0046 | -7.7951 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-1_Q-0.3 | 27.8815 | 38.1426 | DMAT Charging
22 | Yes | Case_setup | 1.03 | -0.5 | 0 | 4.53 | 1.21 | 1.1014 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -12.9153 | -4.6981 |  |  | -13.0014 | -0.0032 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-0.5_Q0 | 20.7188 | 34.0145 | DMAT Charging
23 | Yes | Case_setup | 1.03 | -0.5 | 0 | 7.06 | 1.63 | 1.0675 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | -12.9129 | -4.6917 |  |  | -12.9990 | 0.0036 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-0.5_Q0 | 27.6018 | 37.7482 | DMAT Charging
24 | Yes | Case_setup | 1.03 | -0.05 | 0 | 4.53 | 1.21 | 1.0368 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -1.2782 | -5.6488 |  |  | -1.3033 | 0.0060 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-0.05_Q0 | 20.5223 | 28.1478 | DMAT Charging
25 | Yes | Case_setup | 1.03 | -0.05 | 0 | 7.06 | 1.63 | 1.0336 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -1.2783 | -5.6404 |  |  | -1.3035 | 0.0145 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-0.05_Q0 | 27.4587 | 37.5278 | DMAT Charging
26 | Yes | Case_setup | 1.03 | -0.05 | 0 | 1 | 14 | 1.0341 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -1.2769 | -5.6411 |  |  | -1.3020 | 0.0134 | PSSE_DMAT_BESSC_SCR1_XR14_P-0.05_Q0 | 15.2149 | 14.4948 | DMAT Charging
27 | Yes | Case_setup | 1.03 | -0.05 | 0 | 1 | 3 | 1.0457 | 1.0300 | 1.0000 | -0.0000 | -0.0000 | -1.2762 | -5.6359 |  |  | -1.3013 | 0.0191 | PSSE_DMAT_BESSC_SCR1_XR3_P-0.05_Q0 | 15.4826 | 14.6776 | DMAT Charging
28 | Yes | Case_setup | 1.03 | -0.5 | 0 | 3 | 14 | 1.0538 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | -12.9144 | -4.6838 |  |  | -13.0005 | 0.0117 | PSSE_DMAT_BESSC_SCR3_XR14_P-0.5_Q0 | 14.6431 | 19.9737 | DMAT Charging
29 | Yes | Case_setup | 1.03 | -0.5 | 0 | 3 | 3 | 1.0919 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -12.9161 | -4.6818 |  |  | -13.0022 | 0.0137 | PSSE_DMAT_BESSC_SCR3_XR3_P-0.5_Q0 | 15.2732 | 21.5758 | DMAT Charging
30 | Yes | Case_setup | 1.03 | -1 | 0.395 | 4.53 | 1.21 | 1.1228 | 1.0500 | 1.0500 | 0.0000 | -0.0000 | -25.6894 | 9.3309 |  |  | -26.0000 | 10.2792 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-1_Q0.395 | 20.5989 | 34.7059 | DMAT Charging
31 | Yes | Case_setup | 1.03 | -1 | -0.395 | 4.53 | 1.21 | 1.2369 | 1.0100 | 0.9625 | -0.0000 | 0.0000 | -25.6844 | -11.6064 |  |  | -26.0001 | -10.2841 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-1_Q-0.395 | 21.0770 | 25.9089 | DMAT Charging
32 | Yes | Case_setup | 1.03 | -1 | 0.395 | 7.06 | 1.63 | 1.0656 | 1.0500 | 1.0500 | 0.0000 | 0.0000 | -25.6888 | 9.3246 |  |  | -25.9993 | 10.2733 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-1_Q0.395 | 27.3677 | 37.4615 | DMAT Charging
33 | Yes | Case_setup | 1.03 | -1 | -0.395 | 7.06 | 1.63 | 1.1516 | 1.0100 | 0.9625 | -0.0000 | -0.0000 | -25.6850 | -11.5895 |  |  | -26.0005 | -10.2641 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-1_Q-0.395 | 27.9954 | 36.3384 | DMAT Charging
34 | Yes | Case_setup | 1.03 | -0.05 | 0 | 10 | 3 | 1.0315 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -1.2780 | -5.6385 |  |  | -1.3031 | 0.0163 | PSSE_DMAT_BESSC_SCR10_XR3_P-0.05_Q0 | 34.6569 | 47.2308 | DMAT Charging
35 | Yes | Case_setup | 1.03 | -1 | 0 | 1000 | 10 | 1.0301 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | -25.7269 | -1.8144 |  |  | -25.9979 | 0.0165 | PSSE_DMAT_BESSC_SCR1000_XR10_P-1_Q0 | 2669.7598 | 3608.4802 | DMAT Charging
36 | Yes | Case_setup | 1.03 | -1 | -0.395 | 1000 | 10 | 1.0305 | 1.0100 | 0.9625 | 0.0000 | -0.0000 | -25.6873 | -11.5799 |  |  | -26.0027 | -10.2537 | PSSE_DMAT_BESSC_SCR1000_XR10_P-1_Q-0.395 | 2670.1596 | 3603.6140 | DMAT Charging
37 | Yes | Case_setup | 1.03 | -0.01 | 0.395 | 1000 | 10 | 1.0296 | 1.0500 | 1.0500 | 0.0000 | -0.0000 | -0.2164 | 5.1180 |  |  | -0.2594 | 10.2799 | PSSE_DMAT_BESSC_SCR1000_XR10_P-0.01_Q0.395 | 2669.3382 | 3607.7580 | DMAT Charging
38 | Yes | Case_setup | 1.03 | -0.01 | -0.395 | 1000 | 10 | 1.0304 | 1.0100 | 0.9625 | 0.0000 | -0.0000 | -0.1766 | -15.1422 |  |  | -0.2605 | -10.2501 | PSSE_DMAT_BESSC_SCR1000_XR10_P-0.01_Q-0.395 | 2666.6727 | 3601.4475 | DMAT Charging
39 | Yes | Case_setup | 1.03 | -1 | 0 | 1 | 14 | 1.0000 | 1.2762 | 1.0125 | 0.0000 | -0.0000 | -25.6607 | 20.6214 |  |  | -25.9557 | 24.1780 | PSSE_DMAT_BESSC_SCR1_XR14_P-1_Q0 | -1.9789 | -1.0517 | DMAT Charging
40 | Yes | Case_setup | 1.03 | -1 | 0 | 1 | 3 | 1.0000 | 0.6043 | 1.0000 | -0.0000 | -0.0000 | 1.0000 | -5.1838 |  |  | 0.9761 | 0.5215 | PSSE_DMAT_BESSC_SCR1_XR3_P-1_Q0 | 13.6454 | -113214922307164700672.0000 | DMAT Charging
41 | Yes | Case_setup | 1.03 | -1 | 0 | 5 | 6 | 1.0789 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | -25.7269 | -1.8118 |  |  | -25.9980 | 0.0193 | PSSE_DMAT_BESSC_SCR5_XR6_P-1_Q0 | 19.9247 | 27.1154 | DMAT Charging
42 | Yes | Case_setup | 1.03 | -0.05 | 0 | 5 | 6 | 1.0315 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -1.2783 | -5.6413 |  |  | -1.3034 | 0.0132 | PSSE_DMAT_BESSC_SCR5_XR6_P-0.05_Q0 | 19.9532 | 27.1548 | DMAT Charging
43 | Yes | Case_setup | 1.03 | -1 | 0 | 10 | 6 | 1.0503 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | -25.7273 | -1.8145 |  |  | -25.9984 | 0.0162 | PSSE_DMAT_BESSC_SCR10_XR6_P-1_Q0 | 33.8336 | 46.0626 | DMAT Charging
44 | Yes | Case_setup | 1.03 | -1 | 0 | 3 | 6 | 1.1291 | 1.0300 | 1.0000 | -0.0000 | -0.0000 | -25.7267 | -1.8210 |  |  | -25.9978 | 0.0095 | PSSE_DMAT_BESSC_SCR3_XR6_P-1_Q0 | 14.6422 | 19.9748 | DMAT Charging
45 | Yes | Case_setup | 1.03 | -0.05 | -0.3 | 7.06 | 1.63 | 1.0688 | 1.0148 | 0.9750 | 0.0000 | -0.0000 | -1.2371 | -12.8952 |  |  | -1.3011 | -7.7825 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-0.05_Q-0.3 | 27.6103 | 34.4959 | DMAT Charging
46 | Yes | Case_setup | 1.03 | -0.05 | 0.3 | 7.06 | 1.63 | 0.9988 | 1.0452 | 1.0250 | 0.0000 | 0.0000 | -1.2719 | 2.2659 |  |  | -1.3026 | 7.8010 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P-0.05_Q0.3 | 27.3307 | 37.3628 | DMAT Charging
47 | Yes | Case_setup | 1.03 | -0.05 | -0.3 | 4.53 | 1.21 | 1.0869 | 1.0148 | 0.9750 | 0.0000 | -0.0000 | -1.2395 | -12.9065 |  |  | -1.3036 | -7.7957 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-0.05_Q-0.3 | 20.3466 | 24.5206 | DMAT Charging
48 | Yes | Case_setup | 1.03 | -0.05 | 0.3 | 4.53 | 1.21 | 0.9885 | 1.0452 | 1.0250 | -0.0000 | -0.0000 | -1.2714 | 2.2690 |  |  | -1.3021 | 7.8044 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P-0.05_Q0.3 | 20.4528 | 28.0646 | DMAT Charging
49 | Yes | Case_setup | 1.03 | 0 | 0 | 3 | 14 | 1.0298 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 0.0214 | -5.6487 |  |  | -0.0031 | 0.0179 | PSSE_DMAT_BESSC_SCR3_XR14_P0_Q0 | 14.6672 | 20.0067 | SMIB
50 | Yes | Case_setup | 1.03 | 0 | 0 | 3 | 3 | 1.0299 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 0.0215 | -5.6565 |  |  | -0.0030 | 0.0096 | PSSE_DMAT_BESSC_SCR3_XR3_P0_Q0 | 14.7899 | 21.4775 | SMIB
51 | Yes | Case_setup | 1.03 | 0 | 0 | 7.06 | 1.63 | 1.0299 | 1.0300 | 1.0000 | -0.0000 | -0.0000 | 0.0233 | -5.6523 |  |  | -0.0012 | 0.0144 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P0_Q0 | 27.4404 | 37.4999 | SMIB
52 | Yes | Case_setup | 1.03 | 0 | 0 | 4.53 | 1.21 | 1.0300 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 0.0218 | -5.6603 |  |  | -0.0027 | 0.0063 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P0_Q0 | 20.4968 | 28.1096 | SMIB
53 | Yes | Case_setup | 1.03 | 0 | 0.395 | 7.06 | 1.63 | 0.9841 | 1.0500 | 1.0375 | -0.0000 | 0.0000 | 0.0411 | 4.9673 |  |  | -0.0012 | 10.2704 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P0_Q0.395 | 27.2332 | 37.2301 | SMIB
54 | Yes | Case_setup | 1.03 | 0 | 0.395 | 4.53 | 1.21 | 0.9662 | 1.0500 | 1.0375 | 0.0000 | 0.0000 | 0.0392 | 4.9733 |  |  | -0.0031 | 10.2767 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P0_Q0.395 | 20.3632 | 27.9446 | SMIB
55 | Yes | Case_setup | 1.03 | 0 | -0.395 | 7.06 | 1.63 | 1.0766 | 1.0100 | 0.9625 | -0.0000 | 0.0000 | 0.0823 | -15.1519 |  |  | -0.0017 | -10.2605 | PSSE_DMAT_BESSC_SCR7.06_XR1.63_P0_Q-0.395 | 25.4062 | 32.1422 | SMIB
56 | Yes | Case_setup | 1.03 | 0 | -0.395 | 4.53 | 1.21 | 1.0966 | 1.0100 | 0.9625 | 0.0000 | -0.0000 | 0.0833 | -15.1565 |  |  | -0.0007 | -10.2660 | PSSE_DMAT_BESSC_SCR4.53_XR1.21_P0_Q-0.395 | 17.6860 | 21.8699 | SMIB
57 | Yes | Case_setup | 1.03 | -1 | 0.395 | 1000 | 10 | 1.0297 | 1.0500 | 1.0500 | 0.0000 | -0.0000 | -25.6878 | 9.3318 |  |  | -25.9984 | 10.2810 | PSSE_DMAT_BESSC_SCR1000_XR10_P-1_Q0.395 | 2669.1709 | 3607.4852 | SMIB Charging
58 | Yes | Case_setup | 1.03 | -1 | -0.395 | 1000 | 10 | 1.0305 | 1.0100 | 0.9625 | 0.0000 | -0.0000 | -25.6873 | -11.5799 |  |  | -26.0027 | -10.2537 | PSSE_DMAT_BESSC_SCR1000_XR10_P-1_Q-0.395 | 2670.1596 | 3603.6140 | SMIB Charging
59 | Yes | Case_setup | 1.03 | 0 | 0.395 | 1000 | 10 | 1.0296 | 1.0500 | 1.0500 | 0.0000 | -0.0000 | 0.0436 | 5.1167 |  |  | 0.0006 | 10.2795 | PSSE_DMAT_BESSC_SCR1000_XR10_P0_Q0.395 | 2669.3351 | 3607.7549 | SMIB
60 | Yes | Case_setup | 1.03 | 0 | -0.395 | 1000 | 10 | 1.0304 | 1.0100 | 0.9625 | -0.0000 | -0.0000 | 0.0834 | -15.1433 |  |  | -0.0005 | -10.2504 | PSSE_DMAT_BESSC_SCR1000_XR10_P0_Q-0.395 | 2666.6758 | 3601.4444 | SMIB
61 | Yes | Case_setup | 1.03 | 1 | 0 | 10 | 3 | 1.0035 | 1.0300 | 1.0125 | 0.0000 | -0.0000 | 26.2750 | -1.6802 |  |  | 25.9981 | 0.0110 | PSSE_DMAT_BESSD_SCR10_XR3_P1_Q0 | 34.1434 | 46.4636 | DMAT Discharging | BESS Discharging
62 | Yes | Case_setup | 1.03 | 1 | 0 | 10 | 14 | 1.0276 | 1.0300 | 1.0125 | 0.0000 | 0.0000 | 26.2789 | -1.6767 |  |  | 26.0019 | 0.0134 | PSSE_DMAT_BESSD_SCR10_XR14_P1_Q0 | 33.3183 | 44.6157 | DMAT Discharging
63 | Yes | Case_setup | 1.03 | 1 | 0.3 | 10 | 14 | 0.9986 | 1.0451 | 1.0375 | 0.0000 | -0.0000 | 26.2924 | 6.3981 |  |  | 25.9990 | 7.7805 | PSSE_DMAT_BESSD_SCR10_XR14_P1_Q0.3 | 33.0750 | 44.2835 | DMAT Discharging
64 | Yes | Case_setup | 1.03 | 1 | -0.3 | 10 | 14 | 1.0567 | 1.0148 | 0.9875 | 0.0000 | -0.0000 | 26.3044 | -9.1010 |  |  | 25.9985 | -7.7852 | PSSE_DMAT_BESSD_SCR10_XR14_P1_Q-0.3 | 33.5824 | 44.8985 | DMAT Discharging
65 | Yes | Case_setup | 1.03 | 1 | 0 | 3 | 14 | 1.0573 | 1.0300 | 1.0125 | 0.0000 | -0.0000 | 26.2750 | -1.6794 |  |  | 25.9981 | 0.0118 | PSSE_DMAT_BESSD_SCR3_XR14_P1_Q0 | 14.3730 | 19.5817 | DMAT Discharging
66 | Yes | Case_setup | 1.03 | 1 | 0 | 3 | 3 | 0.9773 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 26.2723 | -1.9355 |  |  | 26.0003 | -0.0143 | PSSE_DMAT_BESSD_SCR3_XR3_P1_Q0 | 14.3609 | 19.5630 | DMAT Discharging
67 | Yes | Case_setup | 1.03 | 1 | 0.3 | 3 | 3 | 0.8802 | 1.0452 | 1.0375 | 0.0000 | -0.0000 | 26.2894 | 6.4035 |  |  | 25.9961 | 7.7867 | PSSE_DMAT_BESSD_SCR3_XR3_P1_Q0.3 | 14.1451 | 19.2618 | DMAT Discharging
68 | Yes | Case_setup | 1.03 | 1 | -0.3 | 3 | 3 | 1.0741 | 1.0148 | 0.9875 | 0.0000 | -0.0000 | 26.3057 | -9.1031 |  |  | 25.9997 | -7.7879 | PSSE_DMAT_BESSD_SCR3_XR3_P1_Q-0.3 | 14.5875 | 19.6916 | DMAT Discharging
69 | Yes | Case_setup | 1.03 | 0.05 | 0 | 10 | 14 | 1.0296 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | 1.3220 | -5.6449 |  |  | 1.2968 | 0.0144 | PSSE_DMAT_BESSD_SCR10_XR14_P0.05_Q0 | 33.6199 | 44.9199 | DMAT Discharging
70 | Yes | Case_setup | 1.03 | 0.05 | 0.3 | 10 | 14 | 1.0006 | 1.0452 | 1.0250 | -0.0000 | 0.0000 | 1.3308 | 2.2708 |  |  | 1.3000 | 7.8102 | PSSE_DMAT_BESSD_SCR10_XR14_P0.05_Q0.3 | 33.3659 | 44.5731 | DMAT Discharging
71 | Yes | Case_setup | 1.03 | 0.05 | -0.3 | 10 | 14 | 1.0587 | 1.0148 | 0.9750 | -0.0000 | -0.0000 | 1.3626 | -12.9019 |  |  | 1.2986 | -7.7851 | PSSE_DMAT_BESSD_SCR10_XR14_P0.05_Q-0.3 | 33.8955 | 41.8802 | DMAT Discharging
72 | Yes | Case_setup | 1.03 | 0.05 | 0 | 3 | 14 | 1.0288 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 1.3214 | -5.6419 |  |  | 1.2963 | 0.0176 | PSSE_DMAT_BESSD_SCR3_XR14_P0.05_Q0 | 14.6662 | 20.0050 | DMAT Discharging
73 | Yes | Case_setup | 1.03 | 0.05 | 0 | 3 | 3 | 1.0248 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 1.3215 | -5.6404 |  |  | 1.2964 | 0.0193 | PSSE_DMAT_BESSD_SCR3_XR3_P0.05_Q0 | 14.7821 | 21.4557 | DMAT Discharging
74 | Yes | Case_setup | 1.03 | 0.05 | 0.3 | 3 | 3 | 0.9331 | 1.0452 | 1.0250 | 0.0000 | -0.0000 | 1.3289 | 2.2446 |  |  | 1.2982 | 7.7848 | PSSE_DMAT_BESSD_SCR3_XR3_P0.05_Q0.3 | 14.5591 | 19.8674 | DMAT Discharging
75 | Yes | Case_setup | 1.03 | 0.05 | -0.3 | 3 | 3 | 1.1178 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | 1.3634 | -12.9051 |  |  | 1.2993 | -7.7887 | PSSE_DMAT_BESSD_SCR3_XR3_P0.05_Q-0.3 | 14.5924 | 15.8191 | DMAT Discharging
76 | Yes | Case_setup | 1.03 | 1 | 0 | 4.53 | 1.21 | 0.9087 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 26.2727 | -1.9376 |  |  | 26.0007 | -0.0169 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P1_Q0 | 19.8430 | 26.5973 | DMAT Discharging
77 | Yes | Case_setup | 1.03 | 1 | 0.3 | 4.53 | 1.21 | 0.8531 | 1.0452 | 1.0375 | -0.0000 | 0.0000 | 26.2885 | 6.4079 |  |  | 25.9951 | 7.7914 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P1_Q0.3 | 19.6522 | 26.2884 | DMAT Discharging
78 | Yes | Case_setup | 1.03 | 1 | -0.3 | 4.53 | 1.21 | 0.9654 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | 26.3049 | -9.3690 |  |  | 26.0040 | -7.8094 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P1_Q-0.3 | 20.0207 | 26.8539 | DMAT Discharging
79 | Yes | Case_setup | 1.03 | 1 | 0 | 7.06 | 1.63 | 0.9653 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | 26.2757 | -1.9345 |  |  | 26.0037 | -0.0145 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P1_Q0 | 26.9779 | 36.8405 | DMAT Discharging
80 | Yes | Case_setup | 1.03 | 1 | 0.3 | 7.06 | 1.63 | 0.9279 | 1.0452 | 1.0375 | -0.0000 | -0.0000 | 26.2890 | 6.4099 |  |  | 25.9957 | 7.7931 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P1_Q0.3 | 26.7349 | 36.4874 | DMAT Discharging
81 | Yes | Case_setup | 1.03 | 1 | -0.3 | 7.06 | 1.63 | 1.0029 | 1.0148 | 0.9875 | -0.0000 | 0.0000 | 26.3042 | -9.1059 |  |  | 25.9982 | -7.7906 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P1_Q-0.3 | 26.9893 | 36.8930 | DMAT Discharging
82 | Yes | Case_setup | 1.03 | 0.5 | 0 | 4.53 | 1.21 | 0.9653 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 13.0902 | -4.7437 |  |  | 13.0037 | -0.0033 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P0.5_Q0 | 20.2046 | 27.6700 | DMAT Discharging
83 | Yes | Case_setup | 1.03 | 0.5 | 0 | 7.06 | 1.63 | 0.9958 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 13.0892 | -4.7544 |  |  | 13.0026 | -0.0146 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P0.5_Q0 | 27.2320 | 37.1822 | DMAT Discharging
84 | Yes | Case_setup | 1.03 | 0.05 | 0 | 4.53 | 1.21 | 1.0233 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 1.3218 | -5.6652 |  |  | 1.2966 | -0.0070 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P0.05_Q0 | 20.4705 | 28.0698 | DMAT Discharging
85 | Yes | Case_setup | 1.03 | 0.05 | 0 | 7.06 | 1.63 | 1.0264 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 1.3233 | -5.6456 |  |  | 1.2981 | 0.0139 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P0.05_Q0 | 27.4216 | 37.4713 | DMAT Discharging
86 | Yes | Case_setup | 1.03 | 0.05 | 0 | 1 | 14 | 1.0273 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 1.3231 | -5.6475 |  |  | 1.2979 | 0.0116 | PSSE_DMAT_BESSD_SCR1_XR14_P0.05_Q0 | 15.1876 | 14.4668 | DMAT Discharging
87 | Yes | Case_setup | 1.03 | 0.05 | 0 | 1 | 3 | 1.0154 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 1.3238 | -5.6495 |  |  | 1.2986 | 0.0095 | PSSE_DMAT_BESSD_SCR1_XR3_P0.05_Q0 | 15.4360 | 14.6129 | DMAT Discharging
88 | Yes | Case_setup | 1.03 | 0.5 | 0 | 3 | 14 | 1.0310 | 1.0300 | 1.0125 | 0.0000 | -0.0000 | 13.0829 | -4.5630 |  |  | 12.9954 | 0.0181 | PSSE_DMAT_BESSD_SCR3_XR14_P0.5_Q0 | 14.4752 | 19.7353 | DMAT Discharging
89 | Yes | Case_setup | 1.03 | 0.5 | 0 | 3 | 3 | 0.9910 | 1.0300 | 1.0000 | 0.0000 | -0.0000 | 13.0871 | -4.7598 |  |  | 13.0006 | -0.0199 | PSSE_DMAT_BESSD_SCR3_XR3_P0.5_Q0 | 14.6831 | 20.0294 | DMAT Discharging
90 | Yes | Case_setup | 1.03 | 1 | 0.395 | 4.53 | 1.21 | 0.8357 | 1.0500 | 1.0500 | 0.0000 | 0.0000 | 26.3074 | 9.2298 |  |  | 25.9961 | 10.2692 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P1_Q0.395 | 19.1602 | 26.2128 | DMAT Discharging
91 | Yes | Case_setup | 1.03 | 1 | -0.395 | 4.53 | 1.21 | 0.9835 | 1.0100 | 0.9750 | 0.0000 | -0.0000 | 26.3215 | -11.4413 |  |  | 25.9995 | -10.2815 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P1_Q-0.395 | 19.9987 | 26.3256 | DMAT Discharging
92 | Yes | Case_setup | 1.03 | 1 | 0.395 | 7.06 | 1.63 | 0.9161 | 1.0500 | 1.0500 | -0.0000 | -0.0000 | 26.3075 | 9.2252 |  |  | 25.9962 | 10.2647 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P1_Q0.395 | 26.6623 | 36.3927 | DMAT Discharging
93 | Yes | Case_setup | 1.03 | 1 | -0.395 | 7.06 | 1.63 | 1.0148 | 1.0100 | 0.9750 | -0.0000 | 0.0000 | 26.3207 | -11.4236 |  |  | 25.9989 | -10.2599 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P1_Q-0.395 | 27.1090 | 35.9277 | DMAT Discharging
94 | Yes | Case_setup | 1.03 | 0.05 | 0 | 10 | 3 | 1.0284 | 1.0300 | 1.0000 | -0.0000 | 0.0000 | 1.3219 | -5.6442 |  |  | 1.2967 | 0.0153 | PSSE_DMAT_BESSD_SCR10_XR3_P0.05_Q0 | 34.6335 | 47.1952 | DMAT Discharging
95 | Yes | Case_setup | 1.03 | 1 | 0 | 1000 | 10 | 1.0299 | 1.0300 | 1.0125 | -0.0000 | -0.0000 | 26.2789 | -1.6762 |  |  | 26.0019 | 0.0140 | PSSE_DMAT_BESSD_SCR1000_XR10_P1_Q0 | 2669.4064 | 3607.9130 | DMAT Discharging
96 | Yes | Case_setup | 1.03 | 1 | -0.395 | 1000 | 10 | 1.0303 | 1.0100 | 0.9750 | 0.0000 | 0.0000 | 26.3200 | -11.4192 |  |  | 25.9983 | -10.2544 | PSSE_DMAT_BESSD_SCR1000_XR10_P1_Q-0.395 | 2669.6358 | 3603.4746 | DMAT Discharging
97 | Yes | Case_setup | 1.03 | 0.01 | 0.395 | 1000 | 10 | 1.0296 | 1.0500 | 1.0500 | 0.0000 | 0.0000 | 0.3036 | 5.1198 |  |  | 0.2606 | 10.2824 | PSSE_DMAT_BESSD_SCR1000_XR10_P0.01_Q0.395 | 2669.3320 | 3607.7518 | DMAT Discharging
98 | Yes | Case_setup | 1.03 | 0.01 | -0.395 | 1000 | 10 | 1.0304 | 1.0100 | 0.9625 | -0.0000 | 0.0000 | 0.3434 | -15.1491 |  |  | 0.2595 | -10.2572 | PSSE_DMAT_BESSD_SCR1000_XR10_P0.01_Q-0.395 | 2666.6634 | 3601.4351 | DMAT Discharging
99 | Yes | Case_setup | 1.03 | 1 | 0 | 1 | 14 | 1.3642 | 1.0300 | 1.0125 | 0.0000 | -0.0000 | 26.2803 | -1.6879 |  |  | 26.0033 | 0.0018 | PSSE_DMAT_BESSD_SCR1_XR14_P1_Q0 | 13.3314 | 13.1334 | DMAT Discharging
100 | Yes | Case_setup | 1.03 | 1 | 0 | 1 | 3 | 1.1707 | 1.0300 | 1.0125 | -0.0000 | -0.0000 | 26.2754 | -1.6858 |  |  | 25.9985 | 0.0050 | PSSE_DMAT_BESSD_SCR1_XR3_P1_Q0 | 13.2160 | 12.9341 | DMAT Discharging
101 | Yes | Case_setup | 1.03 | 1 | 0 | 5 | 6 | 1.0162 | 1.0300 | 1.0125 | -0.0000 | -0.0000 | 26.2721 | -1.6762 |  |  | 25.9953 | 0.0161 | PSSE_DMAT_BESSD_SCR5_XR6_P1_Q0 | 19.6369 | 26.6936 | DMAT Discharging
102 | Yes | Case_setup | 1.03 | 0.05 | 0 | 5 | 6 | 1.0284 | 1.0300 | 1.0000 | 0.0000 | 0.0000 | 1.3217 | -5.6467 |  |  | 1.2965 | 0.0125 | PSSE_DMAT_BESSD_SCR5_XR6_P0.05_Q0 | 19.9464 | 27.1442 | DMAT Discharging
103 | Yes | Case_setup | 1.03 | 1 | 0 | 10 | 6 | 1.0185 | 1.0300 | 1.0125 | 0.0000 | 0.0000 | 26.2795 | -1.6725 |  |  | 26.0026 | 0.0177 | PSSE_DMAT_BESSD_SCR10_XR6_P1_Q0 | 33.4758 | 44.8854 | DMAT Discharging
104 | Yes | Case_setup | 1.03 | 1 | 0 | 3 | 6 | 1.0275 | 1.0300 | 1.0125 | -0.0000 | -0.0000 | 26.2765 | -1.6766 |  |  | 25.9996 | 0.0143 | PSSE_DMAT_BESSD_SCR3_XR6_P1_Q0 | 14.3563 | 19.5565 | DMAT Discharging
105 | Yes | Case_setup | 1.03 | 0.05 | -0.3 | 7.06 | 1.63 | 1.0618 | 1.0148 | 0.9750 | 0.0000 | 0.0000 | 1.3637 | -12.9009 |  |  | 1.2997 | -7.7836 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P0.05_Q-0.3 | 27.5722 | 34.4373 | DMAT Discharging
106 | Yes | Case_setup | 1.03 | 0.05 | 0.3 | 7.06 | 1.63 | 0.9914 | 1.0452 | 1.0250 | -0.0000 | -0.0000 | 1.3281 | 2.2580 |  |  | 1.2974 | 7.7979 | PSSE_DMAT_BESSD_SCR7.06_XR1.63_P0.05_Q0.3 | 27.2949 | 37.3079 | DMAT Discharging
107 | Yes | Case_setup | 1.03 | 0.05 | -0.3 | 4.53 | 1.21 | 1.0738 | 1.0148 | 0.9750 | 0.0000 | -0.0000 | 1.3608 | -12.9096 |  |  | 1.2967 | -7.7937 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P0.05_Q-0.3 | 20.3025 | 24.3631 | DMAT Discharging
108 | Yes | Case_setup | 1.03 | 0.05 | 0.3 | 4.53 | 1.21 | 0.9742 | 1.0452 | 1.0250 | 0.0000 | 0.0000 | 1.3292 | 2.2617 |  |  | 1.2984 | 7.8017 | PSSE_DMAT_BESSD_SCR4.53_XR1.21_P0.05_Q0.3 | 20.4022 | 27.9880 | DMAT Discharging
109 | Yes | Case_setup | 1.03 | 1 | 0.395 | 1000 | 10 | 1.0295 | 1.0500 | 1.0625 | -0.0000 | 0.0000 | 26.3183 | 9.4766 |  |  | 26.0007 | 10.2799 | PSSE_DMAT_BESSD_SCR1000_XR10_P1_Q0.395 | 2668.8764 | 3607.0048 | SMIB Discharging
110 | Yes | Case_setup | 1.03 | 1 | -0.395 | 1000 | 10 | 1.0303 | 1.0100 | 0.9750 | 0.0000 | 0.0000 | 26.3200 | -11.4192 |  |  | 25.9983 | -10.2544 | PSSE_DMAT_BESSD_SCR1000_XR10_P1_Q-0.395 | 2669.6358 | 3603.4746 | SMIB Discharging
111 | Yes | Case_setup | 1 | 1 | 0.395 | 1001 | 10 | 0.9995 | 1.0200 | 1.0250 | -0.0000 | -0.0000 | 26.3154 | 9.3355 |  |  | 25.9994 | 10.2613 | PSSE_DMAT_BESSD_SCR1001_XR10_P1_Q0.395 | 3343.7123 | 4240.8884 | SMIB Discharging
112 | Yes | Case_setup | 1 | 1 | -0.395 | 1001 | 10 | 1.0003 | 0.9800 | 0.9500 | -0.0000 | 0.0000 | 26.3209 | -11.3376 |  |  | 25.9958 | -10.2495 | PSSE_DMAT_BESSD_SCR1001_XR10_P1_Q-0.395 | 3341.7391 | 4234.4754 | SMIB Discharging
113 | Yes | Case_setup | 1 | 0.01 | 0.395 | 1001 | 10 | 0.9996 | 1.0200 | 1.0125 | -0.0000 | 0.0000 | 0.2973 | 5.0123 |  |  | 0.2555 | 10.2545 | PSSE_DMAT_BESSD_SCR1001_XR10_P0.01_Q0.395 | 3344.3391 | 4241.8440 | SMIB Discharging
114 | Yes | Case_setup | 1 | 0.01 | -0.395 | 1001 | 10 | 1.0004 | 0.9800 | 0.9375 | 0.0000 | 0.0000 | 0.3429 | -15.1050 |  |  | 0.2594 | -10.2590 | PSSE_DMAT_BESSD_SCR1001_XR10_P0.01_Q-0.395 | 3339.1873 | 4232.5720 | SMIB Discharging
115 | Yes | Case_setup | 1 | -1 | 0.395 | 1001 | 10 | 0.9997 | 1.0200 | 1.0125 | 0.0000 | 0.0000 | -25.6936 | 9.1824 |  |  | -26.0026 | 10.2580 | PSSE_DMAT_BESSC_SCR1001_XR10_P-1_Q0.395 | 3344.1312 | 4241.5275 | SMIB Charging
116 | Yes | Case_setup | 1 | -1 | -0.395 | 1001 | 10 | 1.0005 | 0.9800 | 0.9375 | 0.0000 | -0.0000 | -25.6828 | -11.5052 |  |  | -26.0015 | -10.2527 | PSSE_DMAT_BESSC_SCR1001_XR10_P-1_Q-0.395 | 3342.0013 | 4234.6104 | SMIB Charging
117 | Yes | Case_setup | 1 | -0.01 | 0.395 | 1001 | 10 | 0.9996 | 1.0200 | 1.0125 | -0.0000 | 0.0000 | -0.2226 | 5.0138 |  |  | -0.2645 | 10.2551 | PSSE_DMAT_BESSC_SCR1001_XR10_P-0.01_Q0.395 | 3344.3391 | 4241.8471 | SMIB Charging
118 | Yes | Case_setup | 1 | -0.01 | -0.395 | 1001 | 10 | 1.0004 | 0.9800 | 0.9375 | 0.0000 | -0.0000 | -0.1772 | -15.1023 |  |  | -0.2606 | -10.2569 | PSSE_DMAT_BESSC_SCR1001_XR10_P-0.01_Q-0.395 | 3339.1966 | 4232.5844 | SMIB Charging

## Inputs
Project Name: | Upper Hunter Hybrid
Project Specific Info | SCC | SCR | XR | R | X | L | Rpu | Xpu
Max GS | 752.7 | 10.66 | 4.88 | 1.0769 | 5.6861 | 0.018099 | 0.024722 | 0.13053 |  | R=V^2/(SCR*MW)*(1/(sqrt(1+XR^2))
Min GS | 394.55 | 6.07 | 4.35 | 2.4735 | 10.7598 | 0.034249 | 0.056784 | 0.24701
|  | 10 | 3 | 2.1192 | 6.3576 | 0.020237 | 0.04865 | 0.14595
|  | 10 | 14 | 0.47746 | 6.6845 | 0.021277 | 0.010961 | 0.15346
|  | 3 | 14 | 1.5915 | 22.2817 | 0.070925 | 0.036537 | 0.51152
|  | 3 | 3 | 7.064 | 21.1921 | 0.067457 | 0.16217 | 0.4865
|  | 1 | 14 | 4.7746 | 66.8451 | 0.21277 | 0.10961 | 1.5346
|  | 1 | 3 | 21.1921 | 63.5764 | 0.20237 | 0.4865 | 1.4595
Sbase | Upper Hunter Hybrid SCC: 100
POC kV | Upper Hunter Hybrid SCC: 66 | 65 | 19
Plant MVA | Upper Hunter Hybrid SCC: 84; Upper Hunter Hybrid Rpu: Active power SF; Upper Hunter Hybrid Xpu: Active power SF | Active power BESS | Active power BESS | Resultant active power capability | Resultant active power
Plant MW | Upper Hunter Hybrid SCC: 65; Upper Hunter Hybrid Rpu: 1; Upper Hunter Hybrid Xpu: 84 | -1 | -36.2 | 47.8 | 0.73538
Zbase | Upper Hunter Hybrid SCC: 43.56; Upper Hunter Hybrid SCR: (V^2/Sbase); Upper Hunter Hybrid Rpu: 1; Upper Hunter Hybrid Xpu: 84 | -0.5 | -18.1 | 65.9 | 1
| Upper Hunter Hybrid Rpu: 1; Upper Hunter Hybrid Xpu: 84 | -0.05 | -1.81 | 82.19 | 1
| Upper Hunter Hybrid Rpu: 1; Upper Hunter Hybrid Xpu: 84 | -0.01 | -0.362 | 83.638 | 1
BESS RATING MW | Upper Hunter Hybrid SCC: 36.2
BESS RATING MVA | Upper Hunter Hybrid SCC: 21.72
| Upper Hunter Hybrid Xpu: Active power POC | Active power SF | Active power BESS
PV RATING MW | Upper Hunter Hybrid SCC: 84
PV RATING MVA | Upper Hunter Hybrid SCC: 50.4