## Case_Create
Case | Run_test | Test_Type | ActiveP | ReactiveP | SCR | X_R | Vsource_i | PPC_Vref | Trf_Tap | SF_P | SF_Q | BESS_P | BESS_Q | POC_Pflat | POC_Qflat | Test_File_Names | Shunt(1.15pu) | Shunt(1.2pu) | StateCASE | Reference Equations | backup shunts
1 | Yes | Case_setup | 1 | 0 | 10 | 3 | 1.0035 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR10_XR3_P1_Q0 | 35.4238 | 48.8289 | DMAT SF
2 | Yes | Case_setup | 1 | 0 | 10 | 14 | 1.0276 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P1_Q0 | 34.2679 | 44.7793 | DMAT SF
3 | Yes | Case_setup | 1 | 0.3 | 10 | 14 | 0.9986 | 1.0452 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P1_Q0.3 | 35.1017 | 46.4618 | DMAT SF
4 | Yes | Case_setup | 1 | -0.3 | 10 | 14 | 1.0567 | 1.0148 | 0.9875 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P1_Q-0.3 | 32.4486 | 41.3629 | DMAT SF
5 | Yes | Case_setup | 1 | 0 | 3 | 14 | 1.0573 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR3_XR14_P1_Q0 | 15.5920 | 15.4799 | DMAT SF
6 | Yes | Case_setup | 1 | 0 | 3 | 3 | 0.9773 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P1_Q0 | 15.3807 | 19.2784 | DMAT SF
7 | Yes | Case_setup | 1 | 0.3 | 3 | 3 | 0.8802 | 1.0452 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P1_Q0.3 | 15.9806 | 28.1217 | DMAT SF
8 | Yes | Case_setup | 1 | -0.3 | 3 | 3 | 1.0741 | 1.0148 | 0.9875 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P1_Q-0.3 | 12.5719 | 15.6399 | DMAT SF
9 | Yes | Case_setup | 0.05 | 0 | 10 | 14 | 1.0296 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P0.05_Q0 | 34.3220 | 45.9443 | DMAT SF
10 | Yes | Case_setup | 0.05 | 0.3 | 10 | 14 | 1.0006 | 1.0452 | 1.0250 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P0.05_Q0.3 | 35.1722 | 46.2212 | DMAT SF
11 | Yes | Case_setup | 0.05 | -0.3 | 10 | 14 | 1.0587 | 1.0148 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR10_XR14_P0.05_Q-0.3 | 30.6478 | 39.7518 | DMAT SF
12 | Yes | Case_setup | 0.05 | 0 | 3 | 14 | 1.0288 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR3_XR14_P0.05_Q0 | 13.3999 | 18.7797 | DMAT SF
13 | Yes | Case_setup | 0.05 | 0 | 3 | 3 | 1.0249 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P0.05_Q0 | 15.6999 | 20.8172 | DMAT SF
14 | Yes | Case_setup | 0.05 | 0.3 | 3 | 3 | 0.9331 | 1.0452 | 1.0250 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P0.05_Q0.3 | 16.4852 | 21.0104 | DMAT SF
15 | Yes | Case_setup | 0.05 | -0.3 | 3 | 3 | 1.1178 | 1.0148 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P0.05_Q-0.3 | 11.9629 | 14.6779 | DMAT SF
16 | Yes | Case_setup | 1 | 0 | 4.53 | 1.21 | 0.9087 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P1_Q0 | 21.7056 | 31.2869 | DMAT SF
17 | Yes | Case_setup | 1 | 0.3 | 4.53 | 1.21 | 0.8531 | 1.0452 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P1_Q0.3 | 23.2458 | 31.7081 | DMAT SF
18 | Yes | Case_setup | 1 | -0.3 | 4.53 | 1.21 | 0.9654 | 1.0148 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P1_Q-0.3 | 21.4478 | 27.2276 | DMAT SF
19 | Yes | Case_setup | 1 | 0 | 7.06 | 1.63 | 0.9653 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P1_Q0 | 27.7038 | 40.2946 | DMAT SF
20 | Yes | Case_setup | 1 | 0.3 | 7.06 | 1.63 | 0.9279 | 1.0452 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P1_Q0.3 | 27.8680 | 40.2475 | DMAT SF
21 | Yes | Case_setup | 1 | -0.3 | 7.06 | 1.63 | 1.0029 | 1.0148 | 0.9875 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P1_Q-0.3 | 28.1028 | 36.2706 | DMAT SF
22 | Yes | Case_setup | 0.5 | 0 | 4.53 | 1.21 | 0.9653 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0.5_Q0 | 22.3197 | 31.3488 | DMAT SF
23 | Yes | Case_setup | 0.5 | 0 | 7.06 | 1.63 | 0.9958 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0.5_Q0 | 29.0131 | 40.3190 | DMAT SF
24 | Yes | Case_setup | 0.05 | 0 | 4.53 | 1.21 | 1.0233 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0.05_Q0 | 22.9262 | 31.7939 | DMAT SF
25 | Yes | Case_setup | 0.05 | 0 | 7.06 | 1.63 | 1.0264 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0.05_Q0 | 29.4131 | 40.3575 | DMAT SF
26 | Yes | Case_setup | 0.05 | 0 | 1 | 14 | 1.0272 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1_XR14_P0.05_Q0 | -2.7473 | -1.7521 | DMAT SF
27 | Yes | Case_setup | 0.05 | 0 | 1 | 3 | 1.0153 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1_XR3_P0.05_Q0 | -2.2841 | -1.2478 | DMAT SF
28 | Yes | Case_setup | 0.5 | 0 | 3 | 14 | 1.0310 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR3_XR14_P0.5_Q0 | 2.6952 | 5.6638 | DMAT SF
29 | Yes | Case_setup | 0.5 | 0 | 3 | 3 | 0.9910 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P0.5_Q0 | 5.9661 | 8.9523 | DMAT SF
30 | Yes | Case_setup | 1 | 0.395 | 4.53 | 1.21 | 0.8357 | 1.0500 | 1.0500 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P1_Q0.395 | 44.6088 | 52.6244 | DMAT SF
31 | Yes | Case_setup | 1 | -0.395 | 4.53 | 1.21 | 0.9835 | 1.0100 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P1_Q-0.395 | 17.7852 | 24.2597 | DMAT SF
32 | Yes | Case_setup | 1 | 0.395 | 7.06 | 1.63 | 0.9161 | 1.0500 | 1.0500 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P1_Q0.395 | 41.1452 | 49.3529 | DMAT SF
33 | Yes | Case_setup | 1 | -0.395 | 7.06 | 1.63 | 1.0148 | 1.0100 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P1_Q-0.395 | 20.1773 | 28.6525 | DMAT SF
34 | Yes | Case_setup | 0.05 | 0 | 10 | 3 | 1.0284 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR10_XR3_P0.05_Q0 | 23.6556 | 34.1221 | DMAT SF
35 | Yes | Case_setup | 1 | 0 | 1000 | 10 | 1.0299 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P1_Q0 | 2659.6308 | 3595.0782 | DMAT SF
36 | Yes | Case_setup | 1 | -0.395 | 1000 | 10 | 1.0303 | 1.0100 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P1_Q-0.395 | 2650.6052 | 3586.2293 | DMAT SF
37 | Yes | Case_setup | 0.01 | 0.395 | 1000 | 10 | 1.0296 | 1.0500 | 1.0500 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P0.01_Q0.395 | 2666.5270 | 3601.7947 | DMAT SF
38 | Yes | Case_setup | 0.01 | -0.395 | 1000 | 10 | 1.0304 | 1.0100 | 0.9625 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P0.01_Q-0.395 | 2648.3643 | 3584.0225 | DMAT SF
41 | Yes | Case_setup | 1 | 0 | 1 | 14 | 1.3641 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR1_XR14_P1_Q0 | -10.2396 | -8.9525 | DMAT SF
42 | Yes | Case_setup | 1 | 0 | 1 | 3 | 1.1707 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR1_XR3_P1_Q0 | -5.8751 | -4.7108 | DMAT SF
43 | Yes | Case_setup | 1 | 0 | 5 | 6 | 1.0162 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR5_XR6_P1_Q0 | 10.0159 | 14.7794 | DMAT SF
44 | Yes | Case_setup | 0.05 | 0 | 5 | 6 | 1.0284 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR5_XR6_P0.05_Q0 | 8.4814 | 13.2985 | DMAT SF
45 | Yes | Case_setup | 1 | 0 | 10 | 6 | 1.0185 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR10_XR6_P1_Q0 | 24.8420 | 34.4840 | DMAT SF
46 | Yes | Case_setup | 1 | 0 | 3 | 6 | 1.0274 | 1.0300 | 1.0125 | [6 empty] | PSSE_DMAT_SF_SCR3_XR6_P1_Q0 | 3.0447 | 6.0341 | DMAT SF
53 | Yes | Case_setup | 0.05 | -0.3 | 7.06 | 1.63 | 1.0618 | 1.0148 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0.05_Q-0.3 | 10.9751 | 19.6323 | DMAT SF
54 | Yes | Case_setup | 0.05 | 0.3 | 7.06 | 1.63 | 0.9914 | 1.0452 | 1.0250 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0.05_Q0.3 | 25.4114 | 33.8156 | DMAT SF
55 | Yes | Case_setup | 0.05 | -0.3 | 4.53 | 1.21 | 1.0738 | 1.0148 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0.05_Q-0.3 | 4.5919 | 10.9784 | DMAT SF
56 | Yes | Case_setup | 0.05 | 0.3 | 4.53 | 1.21 | 0.9742 | 1.0452 | 1.0250 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0.05_Q0.3 | 19.7833 | 26.2847 | DMAT SF
57 | Yes | Case_setup | 0 | 0 | 3 | 14 | 1.0298 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR3_XR14_P0_Q0 | 2.6399 | 5.6068 | FULL SF SMIB
58 | Yes | Case_setup | 0 | 0 | 3 | 3 | 1.0299 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR3_XR3_P0_Q0 | 3.1387 | 6.2265 | FULL SF SMIB
59 | Yes | Case_setup | 0 | 0 | 4.53 | 1.21 | 1.0300 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0_Q0 | 11.1369 | 17.5349 | FULL SF SMIB
60 | Yes | Case_setup | 0 | 0 | 7.06 | 1.63 | 1.0299 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0_Q0 | 17.4876 | 26.0139 | FULL SF SMIB
61 | Yes | Case_setup | 0 | 0.395 | 4.53 | 1.21 | 0.9662 | 1.0500 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0_Q0.395 | 21.1552 | 27.6734 | FULL SF SMIB
62 | Yes | Case_setup | 0 | -0.395 | 4.53 | 1.21 | 1.0966 | 1.0100 | 0.9625 | [6 empty] | PSSE_DMAT_SF_SCR4.53_XR1.21_P0_Q-0.395 | 1.2796 | 7.6837 | FULL SF SMIB
63 | Yes | Case_setup | 0 | 0.395 | 7.06 | 1.63 | 0.9841 | 1.0500 | 1.0375 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0_Q0.395 | 26.9993 | 35.3836 | FULL SF SMIB
64 | Yes | Case_setup | 0 | -0.395 | 7.06 | 1.63 | 1.0766 | 1.0100 | 0.9625 | [6 empty] | PSSE_DMAT_SF_SCR7.06_XR1.63_P0_Q-0.395 | 7.9673 | 16.6850 | FULL SF SMIB
65 | Yes | Case_setup | 0 | 0.395 | 1000 | 10 | 1.0296 | 1.0500 | 1.0500 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P0_Q0.395 | 2666.5022 | 3601.7699 | FULL SF SMIB
66 | Yes | Case_setup | 0 | -0.395 | 1000 | 10 | 1.0304 | 1.0100 | 0.9625 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P0_Q-0.395 | 2648.3395 | 3584.0008 | FULL SF SMIB
67 | Yes | Case_setup | 1 | 0.395 | 1000 | 10 | 1.0295 | 1.0500 | 1.0625 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P1_Q0.395 | 2668.7400 | 3603.9488 | FULL SF SMIB
68 | Yes | Case_setup | 1 | -0.395 | 1000 | 10 | 1.0303 | 1.0100 | 0.9750 | [6 empty] | PSSE_DMAT_SF_SCR1000_XR10_P1_Q-0.395 | 2650.6052 | 3586.2293 | FULL SF SMIB
69 | Yes | Case_setup | 1 | 0 | 1.2 | 1.21 | 0.8091 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.2_XR1.21_P1_Q0 | 9.2420 | 11.6459 | SSIA
70 | Yes | Case_setup | 1 | 0 | 1.3 | 1.21 | 0.7994 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.3_XR1.21_P1_Q0 | 11.1517 | 13.9621 | SSIA
71 | Yes | Case_setup | 1 | 0 | 1.4 | 1.21 | 0.7952 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.4_XR1.21_P1_Q0 | 12.7656 | 15.8903 | SSIA
72 | Yes | Case_setup | 1 | 0 | 1.5 | 1.21 | 0.7944 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.5_XR1.21_P1_Q0 | 14.1382 | 17.5061 | SSIA
73 | Yes | Case_setup | 1 | 0 | 1.6 | 1.21 | 0.7958 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.6_XR1.21_P1_Q0 | 15.3097 | 18.8583 | SSIA
74 | Yes | Case_setup | 1 | 0 | 1.7 | 1.21 | 0.7988 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.7_XR1.21_P1_Q0 | 16.3211 | 20.0051 | SSIA
75 | Yes | Case_setup | 1 | 0 | 1.8 | 1.21 | 0.8028 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR1.8_XR1.21_P1_Q0 | 17.2073 | 20.9982 | SSIA
76 | Yes | Case_setup | 1 | 0 | 2 | 1.21 | 0.8123 | 1.0300 | 1.0000 | [6 empty] | PSSE_DMAT_SF_SCR2_XR1.21_P1_Q0 | 18.7101 | 22.6292 | SSIA

## Inputs
Project Name: | Middlemount Hybrid
Project Specific Info | SCC | SCR | XR | R | X | L | Rpu | Xpu
Max GS | 752.7 | 10.66 | 4.88 | 1.0769 | 5.6861 | 0.018099 | 0.024722 | 0.13053 |  | R=V^2/(SCR*MW)*(1/(sqrt(1+XR^2))
Min GS | 394.55 | 6.07 | 4.35 | 2.4735 | 10.7598 | 0.034249 | 0.056784 | 0.24701
|  | 10 | 3 | 2.1192 | 6.3576 | 0.020237 | 0.04865 | 0.14595
|  | 10 | 14 | 0.47746 | 6.6845 | 0.021277 | 0.010961 | 0.15346
|  | 3 | 14 | 1.5915 | 22.2817 | 0.070925 | 0.036537 | 0.51152
|  | 3 | 3 | 7.064 | 21.1921 | 0.067457 | 0.16217 | 0.4865
|  | 1 | 14 | 4.7746 | 66.8451 | 0.21277 | 0.10961 | 1.5346
|  | 1 | 3 | 21.1921 | 63.5764 | 0.20237 | 0.4865 | 1.4595
Sbase | Middlemount Hybrid SCC: 100
POC kV | Middlemount Hybrid SCC: 66 | 65 | 19
Plant MVA | Middlemount Hybrid SCC: 84; Middlemount Hybrid Rpu: Active power SF; Middlemount Hybrid Xpu: Active power SF | Active power BESS | Active power BESS | Resultant active power capability | Resultant active power
Plant MW | Middlemount Hybrid SCC: 65; Middlemount Hybrid Rpu: 1; Middlemount Hybrid Xpu: 84 | -1 | -36.2 | 47.8 | 0.73538
Zbase | Middlemount Hybrid SCC: 43.56; Middlemount Hybrid SCR: (V^2/Sbase); Middlemount Hybrid Rpu: 1; Middlemount Hybrid Xpu: 84 | -0.5 | -18.1 | 65.9 | 1
| Middlemount Hybrid Rpu: 1; Middlemount Hybrid Xpu: 84 | -0.05 | -1.81 | 82.19 | 1
| Middlemount Hybrid Rpu: 1; Middlemount Hybrid Xpu: 84 | -0.01 | -0.362 | 83.638 | 1
BESS RATING MW | Middlemount Hybrid SCC: 36.2
BESS RATING MVA | Middlemount Hybrid SCC: 21.72
| Middlemount Hybrid Xpu: Active power POC | Active power SF | Active power BESS
PV RATING MW | Middlemount Hybrid SCC: 84
PV RATING MVA | Middlemount Hybrid SCC: 50.4